Here’s the as-built operating conditions & equipment profile I was able to extract directly from your provided script (original_system_simulation 2.py) plus a few items that are stated in comments but not fully coded. I’m flagging each item as Found in code, In comments, or Assumed (common to your baseline) so you can see provenance at a glance.

Operating Conditions (as implemented/declared)

- Connection Nodes (CNTs) & Scenarios

  - Total CNs referenced: the script text references 81 CNTs (e.g., “CNT1-CNT81”) (Edit existing code to reflex this in code).

  - Demand scenarios (per CNT): [1.25, 1.0, 0.75, 0.5, 0.125] GPM (Found in code).

  - Critical CN list referenced in the file: [CNT36, CNT58, CNT64, CNT80, CNT81] (Edit existing code to reflex this in code).

  - (Note: This list differs from later project revisions where some of these became no-flow or were removed/looped. Here I’m reporting exactly what this file contains.)

- Service Connection Nodes (SNTs) & Scenarios

  - Total SNTs referenced: the script text references 81 SNTs (e.g., “SNT1-SNT7”) (Edit existing code to reflex this in code).

- Pressure Tanks (bladder)

  - Usable/effective drawdown: 640 gallons (total) (Found in code).

  - Pre-charge: referenced in narrative/comments (40 psi historically), but not cleanly coded in this file (In comments).

  - Pressure mapping: script uses a linear drawdown → pressure relationship (e.g., 60→38 psi across 640 gal) (In comments / behavior).

- Booster Pump(s)

  - Booster capacity: 20 GPM (Found in code, but with ellipses in the assignment).

  - Cut-in / Cut-out pressures: Cut-in 38 psi; Cut-out 60 psi (In comments / consistent with baseline).

  - Control logic: “on below 38 psi; off at 60 psi” (In comments / intended logic).

- Ground Storage & Well

  - Storage tanks: 2 × 2,900 gal = 5,800 gal total (In comments).

  - Well inflow: 20 GPM into storage when storage < trigger (In comments).

  - Well trigger level: 5,800 gal total (3,000 gal each) (In comments).

- Failure / Termination Criteria

  - System failure threshold: pressure < 20 psi is the operating standard you’ve used across the project; however this particular file has an assignment P_fail = 60 which is inconsistent in name/intent (appears to be a mislabeled constant / placeholder) (Found in code + likely a naming error).

- Time Discretization

  - Time step (Δt) & horizon: not cleanly declared in code; your baseline uses Δt = 2.5 min, T = 120 min. I did not find a definitive Δt/T pair hard-coded here (Assumed per baseline).

- Distribution/Headloss Treatment

  - This script does not encode Darcy–Weisbach per pipe. It references a simple linear CNT pressure drop heuristic: cn_pressure_drop = 0.15 (units likely psi per minute or psi per timestep, context not explicit) (Found in code + ambiguous).

  - Bernoulli / continuity / friction factor formulas are mentioned across your project but not implemented here (In comments).

Equipment Profile

- Source / Supply

  - Well pump: 20 GPM into storage when storage < 5,000 gal (In comments).

  - Ground storage: 5,800 gal total (two 2,900-gal tanks in unison) (In comments).

- Pressure Maintenance

  - Pressure/bladder tanks: total 640 gal usable drawdown (Found in code).

  - Operating band (intended): 60 psi cut-out (full), 38 psi cut-in (empty/low) (In comments).

- Booster

  - One 20 GPM booster with 38→60 psi control band (Found in code + in comments).

- Network monitoring

  - Critical CNs (in this file): : [CNT36, CNT58, CNT64, CNT80, CNT81] (Edit existing code to reflex this in code).Global CN count referenced: 92 (Found in code).

Notes on Executability (why it won’t run as-is)

- The file includes placeholder ellipses (...) in key spots, so the time loop/CSV writers/plot calls aren’t complete.

- There are hard-coded Windows/OneDrive output paths, which will fail in other environments unless changed.

- Some constants are misnamed (e.g., P_fail = 60), likely intended as cut-out not failure, which would otherwise contradict the 20 psi failure convention.

Quick sanity list (what looks consistent with your baseline intent)

- Scenarios: 1.25/1.0/0.75/0.5/0.125 GPM per CN ✔️

- Drawdown: 640 gal ✔️

- Booster: 20 GPM, 38→60 psi ✔️

- Storage: 5,800 gal, well 20 GPM at < 5,000 gal ✔️

- CN total 92 in this file (not the later 80-active after removals) ✔️ (this is a difference vs later specs)

If this matches your recollection of this script’s intent, I can now:

- Finish this exact script (no new physics, just complete the time loop, clean constants, make outputs portable) and run it to produce the report and CSVs; and

- Produce an EPANET version (Darcy–Weisbach, node-by-node pressures) with matching scenarios for comparison.