# EPANET Technical Report – Vaquero Village Water System

# 1. System Overview

The Vaquero Village water distribution system is modeled using EPANET and Python-based simulation frameworks. The system consists of:
- A single 20 GPM well feeding two 2900-gallon storage tanks (total 5800 gallons).
- Two 320-gallon pressure maintenance bladder tanks (640 gallons total).
- A booster pump (20 GPM capacity) activating at 38 psi.
- Transmission and service lines modeled as 2.5” and 1.5” PVC respectively.
- Critical connection nodes (CN41, CN81, CN89, CN90, CN91, CN92) monitored for pressure and flow.

# 2. Simulation Framework

Hydraulic analysis is based on the Darcy-Weisbach equation for head loss, the Bernoulli equation for energy balance, and continuity principles. Simulation steps include:
- Sequential use of pressure tanks, then storage tanks and well.
- Booster pump supplying additional flow during demand surges.
- Pressure decay mapped to critical CNs.

# 3. Scenarios Modeled

Baseline and upgrade scenarios have been evaluated:
1. Baseline: 20 GPM well, 640 gallons pressure maintenance.
2. Booster pump engagement at 38 psi.
3. Additional booster pump (20 GPM) engaging at 30 psi.
4. Demand variations: 1.25, 1.0, 0.75, 0.5, 0.125 GPM per active CN.
5. System upgrade proposal: additional well (not implemented), extra 640 gallons pressure maintenance, network loops (SN89-SN71, SN90-SN41), removal of CN91/92.

# 4. Critical Node Monitoring

Simulation tracks pressures at:
- CN41 (no flow, reference node)
- CN81 (active consumer node)
- CN89 (no flow, priority for tracking)
- CN90 (no flow, priority for tracking)
- CN91, CN92 (removed in upgrade scenario)

# 5. Results Summary

Outputs include system-wide pressure, volume, and flow rate data over time. CSV exports provide detailed time-step data for all CNs, with emphasis on the six critical nodes. Key findings:
- Pressure tanks provide initial demand coverage until depletion.
- Booster pump maintains minimum pressure until demand exceeds 20 GPM.
- Optimal activation of second booster pump prevents under-pressurization.

# 6. Next Steps

Recommended actions:
- Continue refining EPANET input file (.inp) for Vaquero Village.
- Generate visualization plots of pressure decay and flow distribution.
- Package Python scripts and CSV outputs into reproducible ZIP archives.
- Maintain rolling checkpoint PDFs/Word docs to safeguard against chat collapse.