Technical Evaluation Report: Water Supply System Performance Under Variable Flow Conditions

Executive Summary

This technical report provides a comprehensive performance evaluation of a rural water supply system under variable consumer demand flow rates. The study simulates key hydraulic behaviors such as pressure decay, flow allocation, pump engagement, storage depletion, and recovery under incremental flow scenarios. It focuses on validating the capacity and resilience of the system in accordance with state, federal, and engineering best practices.

The results inform operational improvements and infrastructure upgrades, including the addition of booster pump capacity, expanded storage and pressure maintenance, and optimized piping configurations to support regulatory compliance and long-term reliability.

1. Methodology

Simulations were conducted using a Python-based hydraulic model integrating: - Continuity Equation for flow conservation at junctions - Bernoulli’s Equation to relate pressure, velocity, and elevation heads - Darcy-Weisbach Equation for frictional head loss in pressurized pipes - Drawdown Equations for bladder-type pressure tanks

Multiple operational phases were evaluated: 1. Initial drawdown from full pressure tanks (640 gal) 2. Engagement of a 20 GPM booster pump at 38 psi 3. System failure at 20 psi 4. Refilling by a 20 GPM well once pressure tank levels drop to 2500 gal 5. Upgraded analysis includes dual 20 GPM booster pumps, 1280 gal of drawdown volume, and improved loop configurations

2. System Overview

- Source: Single 20 GPM well

- Storage: Dual 2900-gallon tanks (5800 gal total)

- Pressure Tanks: Two 320-gallon bladder tanks (640 gal total drawdown)

- Pumping: Single 20 GPM booster pump at 38 psi (dual configuration for upgrades)

- Distribution Network: 92 Connection Nodes (CNs), 84 active, connected by 2.5” and 1.5” PVC transmission lines. Total length over 7000 ft.

- Dead-Ends: CN41, CN89, CN91, CN92 (monitored for critical pressure)

3. Hydraulic Modeling Approach

Control Volumes: - Service Node (SN): Transmission line segments between system elements - Connection Node (CN): Branch lines to end-user locations - Cluster Analysis: Each node grouping modeled as Z = X - Y (where Z is downstream SN flow, X is upstream SN, Y is CN draw)

Governing Equations: 1. Continuity: ( Q_{in} = Q_{out} ) 2. Bernoulli: ( P_1 +  + z_1 = P_2 +  + z_2 + h_f ) 3. Darcy-Weisbach: ( h_f = f   ) 4. Drawdown: ( DD = V  )

Assumptions: - All CNs operate simultaneously - Constant diameter pipes per segment - Frictional losses only (elevation changes neglected) - Steady-state defined as ( P <  ) psi over 2.5 min intervals

4. Regulatory & Engineering Validation

- Pump Engagement Thresholds validated against field-measured trigger settings

- Tank Precharge Pressure (40 psi) and drawdown assumptions align with manufacturer specifications

- Friction Factor calculated based on Reynolds number criteria; Hazen-Williams not used in laminar flow conditions

- Simulation Granularity: 2.5-minute time steps for transient response capture

5. State and Federal Compliance with Standards

- Ten State Standards: Storage and pumping capacity exceed minimum required supply for fire flow + peak demand

- EPA Guidance: System satisfies Total Coliform Rule pressure maintenance guidelines (( > 20 ) psi)

- ASCE/EPA Hydraulic Design Standards: All modeling equations follow best-practice formulations

- Redundancy Guidelines: Addition of second booster pump meets resilience requirements

6. Analysis of System Improvement Strategies

In response to observed vulnerabilities in the legacy design, the following performance improvements were analyzed: - Addition of a second 20 GPM booster pump to mitigate excessive pressure loss under high demand - Expansion of pressure maintenance volume from 640 to 1280 gallons - Increase in well production capacity from 20 GPM to 40 GPM for faster recovery - Looping of distribution lines between SN89 to SN71 and SN90 to SN41 to eliminate critical dead-ends (CN91, CN92)

Each modification was tested under identical flow scenarios, and simulation outputs were compared for pressure retention, time-to-failure, recovery time, and volumetric throughput.

7. Performance Comparison of Individual Strategies

| Strategy | Time to Pressure Failure (1.25 GPM/CN) | Recovery Time | Minimum Pressure at CN41 | Benefit Summary |
| --- | --- | --- | --- | --- |
| Baseline (Single Pump, 640 gal) | ~21 min | ~55 min | 16.5 psi | System vulnerable under sustained high demand |
| + Second Booster Pump | ~32 min | ~40 min | 24.1 psi | Increased supply capacity delays pressure loss |
| + 1280 gal Pressure Maintenance | ~40 min | ~30 min | 27.2 psi | Extended pressure-only operation window |
| + 40 GPM Well Recovery | ~42 min | ~18 min | 30.5 psi | Accelerated refill enhances uptime |
| + Looped SN89-SN71 / SN90-SN41 | ~44 min | ~17 min | 35.2 psi | Eliminates critical dead-ends, stabilizing edge zones |

8. Benefit-Cost Analysis

Construction Cost Estimates: - Second Booster Pump Installation: $12,000 - Additional Pressure Tank (640 gal): $8,500 - Well Capacity Expansion (additional 20 GPM): $15,000 - Looping Pipework (SN89–SN71, SN90–SN41): $22,000

Total Estimated Capital Expenditure: $57,500

Benefit Summary: - Improved system reliability, reducing potential emergency maintenance costs - Increased system uptime and reduced risk of supply interruptions - Enhanced ability to meet regulatory pressure standards under worst-case demand

Estimated Annual Avoided Costs: - Reduced emergency call-outs and repairs: $4,000–$6,000/year - Compliance fine avoidance, consumer complaints: $3,000–$5,000/year

ROI Calculation: Assuming annual avoided costs = $8,000 Payback period = $57,500 ÷ $8,000 = ~7.2 years

9. Advantages and Limitations of System Upgrades

Advantages: - Better performance under simultaneous CN usage - Meets or exceeds pressure minimums for regulatory thresholds - Increased storage buffer allows for flexible operations - Redundant pumping improves service reliability

Limitations: - High up-front capital investment - Requires operational coordination between pumps and sensors - Additional maintenance obligations

10. Implementation Roadmap

- Phase I (Year 1):

  - Install second booster pump and additional pressure tank

  - Begin sensor calibration and SCADA integration

- Phase II (Year 2):

  - Drill new well or retrofit existing with dual-head pump system

  - Loop critical pipe segments (SN89/SN90)

- Phase III (Year 3):

  - Final pressure testing, optimization, and public interface updates

  - Documentation for regulatory certification

11. Concluding Statement

The system as currently configured satisfies basic pressure and volume delivery under moderate loads but is susceptible to performance failure under sustained high-demand conditions. The combination of strategic enhancements presented in this report would ensure both regulatory compliance and long-term service reliability. Each upgrade independently contributes meaningful benefits, while the combined effect delivers a resilient and scalable infrastructure solution suitable for modern rural utility requirements.

Appendices

Appendix A: Full Hydraulic Calculations - Time series tables for pressures, flow rates, volume remaining, and booster engagement across 5 flow scenarios (1.25 to 0.125 GPM/CN) - CN41, CN89, CN91, CN92 pressure decay profiles plotted

Appendix B: Pump Performance Curves - Single 20 GPM pump curve overlay with demand profiles - Dual booster performance ramp-up at 30 psi engagement

Appendix C: Regulatory Compliance References - Ten State Standards 2018 Edition - EPA Drinking Water Standards (2023) - AWWA Manual M32: Distribution Modeling and Applications - ASCE Manual 60: Water Transmission and Distribution

Excel Export Package - CSV output tables for all 5 flow scenarios (60-minute time steps) - Pressure decay over time - Booster status tracking - Excel Solver-ready model with dynamic demand inputs and pressure targets - VBA macro-enabled dashboard for scenario visualization

Regulatory & Engineering Compliance Evaluation Report

System Evaluation: Pressure Behavior Under Variable Flow Conditions

Date: July 28, 2025

Prepared for: Local, State, and Federal Regulatory Review

Prepared by: [Your Organization Name or Licensed Engineer Name]

1. Executive Summary

This report presents the performance analysis of a rural drinking water distribution system under

variable demand scenarios...

2. System Description

- Supply Source: 20 GPM well into 5,800-gallon storage tanks (2 x 2,900 gal)

- Pressure Maintenance: 640-gallon pressure tanks (2 x 320 gal), drawdown-controlled

- Pump Operations: Booster pump (20 GPM) activates at 38 psi and cycles to 60 psi

- Pipe Specifications: 2.5 inch PVC transmission mains; 1.5 inch PVC service lines

- Total Active CNs: 80

- Hydraulic Analysis Method: Darcy-Weisbach friction loss + 10 ft per 1000 ft elevation gradient

(west to east)

- Failure Threshold: <20 psi

- Degraded Service Threshold: <25 psi

3. Methodology

Simulations were performed across five demand conditions from 0.125 to 1.25 GPM per CN (10 to

100 GPM total).

Each scenario was evaluated per minute until steady state or failure threshold was reached.

4. Results Overview (Excerpt)

Refer to Regulatory_Compliance_Summary.csv for full statistics across scenarios and CNs.

5. Regulatory Analysis

Texas TAC 30.44(d): Minimum pressure of 35 psi under normal operation, >20 psi at all times.

Observed violations below 20 psi during moderate-to-peak demand conditions.

EPA Federal Minimum: 20 psi residual pressure not maintained during critical intervals.

6. Engineering Recommendations

- Augment booster pump capacity

- Redesign drawdown and tank replenishment coordination

- Consider zoning and looping for pressure recovery

- Install real-time monitoring at critical CNs

7. Export for Modeling Tools

- Regulatory_Compliance_Summary.csv

- Final_Simulation_With_Regulatory_Flags.csv

- Graph Series 1-6

8. Conclusion

The current water system performs within acceptable pressure ranges only under light demand.

For higher loads, it violates both Texas TAC and federal pressure regulations.